## Sheet1
Transformer calculation sheet, by Manfred Mornhinweg
Input data: |  | Iron: | Center leg mm: |  | 100 |  | Design decisions: |  | Flux Density T: |  | 1
|  |  | Stack height mm: |  | 150 |  |  |  | mm2/A: |  | 0.5
|  |  | Loss W/kg@1T,50Hz: |  | 2 |  |  |  | Fill factor: |  | 0.4
[9 empty] | Temperature rise K: |  | 70
|  |  | Primary V: |  | 230
|  |  | Secondary no-load V: |  | 2000
|  |  | Frequency Hz: |  | 50
[7 empty] | Prices: |  | Iron $/kg |  | 3.2
[9 empty] | Copper $/kg |  | 16
Output data: |  | Cross section mm2: |  | 15000 |  | Window area mm2: |  | 7500 |  | Copper area mm2: |  | 3000
|  | Turns per Volt: |  | 0.3003 |  | Av. turn length mm: |  | 657.0796
| Primary | turns: | 69.0691 |  | Length m: | 45.3839 |  | mm2: | 21.7174 |  | Ampere: | 43.4348
| Secondary | turns: | 600.6006 |  | Length m: | 394.6424 |  | mm2: | 2.4975 |  | Ampere: | 4.995
| Input power VA: |  | 9990 | [5 empty] | Iron loss W: |  | 138.6
| Power loss %: |  | 2.966 | [5 empty] | Copper loss W: |  | 157.6991
| Voltage drop %: |  | 1.5786 | [5 empty] | Total loss W: |  | 296.2991
| Loaded Vout: |  | 1968.4286 | [5 empty] | Surface area m2: |  | 0.3154
[7 empty] | Required thermal transfer coefficient W/m2K: |  |  |  | 13.4206
| Iron weight kg: |  | 69.3 | [6 empty] | 7 is easy to get
| Copper weight kg: |  | 17.6032 | [6 empty] | Convection cooling up to 12
| Cost $: |  | 503.4106 | [6 empty] | Strong fan up to 30
| $/W: |  | 0.050391 | [6 empty] | Oil up to 50?